## Subramanya arcade T 1 -Nxgen -5
Index | [7 empty] | Date | 2026-09-25 19:25
Slno | Facility Name | Client Name | Date Given | Floor | Area/Location | Category | Check Points | Status (Open/Close) | Snag Points | Priority | Ref. Images | Ref. Images | Date Closed | Closed Images | Vendor Name | Project SPOC | Transition SPOC
1 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is all Lights installed and working condition as per the drawings/Design/RCP | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
2 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is Emergency lights is available and working condition for all areas as per drawing/Design with identification | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
1 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is all lights installed without any loose connection or Hanging wires with alignment | Open | Light gap to be closed. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
4 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is all area Lights installed without darkness of area | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
5 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is Lux level is achieving as per the design/Drawings (Standard to be done ) | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
6 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is Lighting sensors installed in each enclose room with good working condition | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
2 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is client logo lights good working condition | Open | Switch indicator not glowing to be rectified at workstation. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
8 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is proper support is provided in 2x2 Lights install in Grid ceiling | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
9 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is all temporary lights and cablesis removed | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
10 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is lights should not installed different type (like Cool,Warm,Milky white like ) | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
3 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is all Raw power, UPS power and EL DB is installed and working conditon as per the SLD/design/drawings | Open | SLD to be installed. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
4 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is all Raw and UPS power DB proper addressing/Nomenclature is installed | Open | As per drawing 40 A to be installed instead of 25A in DB. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
5 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is the DB frame and door properly fixed without any damages and easily access the DB without any obstruction | Open | Gap to be closed in the DB area. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
14 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is UPS industrial socket is provided in Hub room | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
15 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is all UPS and Raw power DB's are connected to earthing and value should be less then 3 ohms | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
16 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | If Dedicated client earthpit to be check if anthing is there | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
17 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is all conduits is running in Raceway/Cable tray | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
18 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is Loose wire should not be Hanging condition in floor | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
19 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is UPS point is available for wi-fi router , Biometeric system,RFS system,VMS ,Projector , TV all meeting rooms | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
20 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is floor wise meter reading installed withdual source energy meters connected properly & DG sensing cable connection to meter | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
6 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Electrical | Is Raw power socket is provided in Workstation area, common area for Vaccum machine purpose | Open | Workstation raceway tray to be installed properly. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
7 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | Electrical room | Electrical | Is the Electrical shock proof rubber mats available in electrical room | Open | Proper mats to be installed for electrical room. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
8 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is Workstation and Meeting room Popup boxed properly fixed without any Hanging condition | Open | Network 1 no of screw missed - Workstation. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
9 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is UPS power provision is provided AHU fire Damper control panel | Open | Panel cover to be fixed. | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
10 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is the Gland with earthing is installed in all cable wherever entry to DB/Panel/MCB's | Open | Tagging & gland Earthing to be installed. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
11 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is All electrical Cable Incoming/ Outgoing tagging is done | Open | Cable to be removedd. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
12 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is all Electrical standard awareness signages installed (415V danger sign need to be placed LT panel and DB) | Open | Sticker to be changed as EL DB. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
28 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is Emergency rescue & first aid procedure installed at LT room (local language, English or hindi) | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
29 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is the Raised floor supporting rod (for structure) need to be connected to earthing plate. (As per CDCP & Safety guidelines) | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
13 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is Body of server rack ,False flooring and other equipment to be connected to earthing strips | Open | Sticker to be installed for server rack. | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
31 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Is A/c outdoor unit area isolator box is 65/68 model-water/weather proof provided | Open |  | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
14 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | Mr cabin | Electrical | Is All Exhaust /Fresh air Fan switches control install in accessible height | Open | Mr cabin 1 missed switch plate to be installed. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
15 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Electrical | Is ferrule is provided end to end with necessary power circuit numbering for DB's | Open | Gaps to be closed in DB. | Medium |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
16 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Interior | Is All extra thread rods trimmed in all supports (tray, copper pipe and etc...) | Open | Proper insulation to be done for copper pipe & drain. | Medium | Media file not included in ZIP export |  |  |  | Interior | Project SPOC | Transition SPOC
35 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is All ac units /Duct is installed as per the drawings | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
17 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Hvac | Is Fresh/Exhaust system provision is done as per the drawing | Open | 40 A to be installed as per drawing in udb. | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
37 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is all Ac remotes has been fixed in the cabins for all indoor units | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
18 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Hvac | Is all Supply and return Diffuser installed and identification is done | Open | Supply & return sticker. | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
39 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is air Balancing is completed and achieving CFM as per Design | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
40 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is all the area's Temperature is achieving 21' to 23 degree | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
41 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Co2 Level achieving below 1000PPM all the area | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
42 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | is trap door is available for Ac units where ever requried with provion for access for services | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
19 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Hvac | Is the DB Level is achiveing all area below 45 DB | Open | Gap to be rectified at DB. | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
44 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Ac unit timer is available for Dual/Standy by units | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
45 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Reception,Cafeteria and Coworking area Ac unit Timer to be install | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
46 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is All Critical room working and stand by unit installed (ISP(Hub room),UPS..Any other ) | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
47 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is ensure no water Leakage from the ac units /Drain pipe with U trap | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
48 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Exhaust fan is installed in Pantry area | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
49 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is near outdoor unit proper condensation is Happening (Temp <35) | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
20 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Hvac | Is VCD availability for all the duct branches with Open/Close signages (stickers ) | Open | Vcd sticker required. | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
51 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is butterfly damper availability for AC inlet ducts | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
52 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Z (L) type Ducts installed for return air path in enclosed cabin | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
53 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is indoor and outdoor names and Rubber pads and all Screws installed | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
54 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Ac outdoor units Condenser coil is good condition without any damages and body earthing to be connected | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
55 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Ac unit and drain pipe should not install above Electrical Panel (Server rack, Electrical panel and other Electriacal equipements) | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
56 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is insulation of the duct to be installed inside the duct as per drawings | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
57 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Ac Unit trap door - inside -Accoustic needs to be done to controll the noise and all corner with support to be provided | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
58 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Canvas installed in ahu / duct mouth with Jip | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
59 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is All Ac units swings is working condition without any abnormal noise | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
60 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Actuator is working condition ( Chill water & Fire damper ) | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
61 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Fire Damper is installed for Critical rooms in Centralised Ducts ruuning to Critical rooms | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
62 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Trap door is installed for Compact Cassette unit which is installed in gypsum ceiling | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
63 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Rodent entry point | Is all opening should be closed which is made for Fresh air ducts , Exhaust dusts and copper pipe entry with same colour of the painting and water proof | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
64 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Cowl Pices with Mesh for the Fresh/Exhaust ducts in Outside installed to rain water should not entry | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
65 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is VFD is installed and working condition in AHU | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
66 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is VFD/ AHU is working condition in Auto /manual mode | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
67 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU is running in Bypass mode without VFD | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
68 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU Filter is installed with good and clean | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
69 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU room neat and clean and running in Dust free condition | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
70 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU Fire Damper -Actuator installed with Fire control panel | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
71 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU -Chiller Inlet /outlet Pressure guage ,Thermoguage is installed | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
72 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU Thermostat is installed and connected with Balacing valve | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
73 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU -Chiller line Y stainer is installed in AHU Chiller inlet | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
74 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU -Chiller line Buttery valve is installed in inlet/outlet | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
75 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU -Chiller line BTU meter is installed and working condition | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
21 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Hvac | Is AHU room Fresh air provision is available | Closed | Fresh air filter not available. | High | Media file not included in ZIP export |  | 25/07/2026 |  | IND Aircon | Project SPOC | Transition SPOC
77 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU room proper accoustic is installed | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
78 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Water Tap is available in AHU room for filter cleaning | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
79 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Drain trap is available for AC fiiter cleaning | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
80 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Rubber pads in installed below AHU | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
81 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is FCU coil is good conditon without any damages | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
82 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU door limit switch is working condition | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
83 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is inside AHU -Lights is installed and working condtion | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
84 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is emergency Push button is installed | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
85 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is Duct silencer/Sound attentuatore installed as per drawing | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
86 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Is AHU inside motor abnormal noise and belt tension and UV light availability and working condition | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
87 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Number of ODU and Total capacity of ODU to be mentioned | Open |  | Medium |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
88 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Smoke Detector, speaker ,MCP and Hooter is installed as per the drawings including cabins with access hight | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
89 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is all Smoker detector ,MCP, sprinkler and Hooter is working condition with proper addressing/Numbering | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
90 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is amplifier system is working condition with all speaker and console without auto annocement | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
91 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Fire Exinguisher Suitable standard available, FE Pressure is proper level, detail card is available and security checking and signature done as per drawings | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
92 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is kichan area K Type fire extingusher installed | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
93 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Fire panel -Loop card capacity checked as per detectors installed | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
94 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is amplifier capacity to be checked and speaker quantity to be checked | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
95 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is music system cable to be layed separatly for PA controller for cafeteria , Reception, common Pantry, lift lobby and Rest room | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
22 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Fire Safety | Is Fire exit signage installed as per the drawing | Open | Rp - Main , Y & B circuit 40 A to be installed as per drawing. | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
97 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Fire escape route plan is installed with emmergency contact number | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
98 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Panic bar and buzzer with the signage installed in the fire exit door | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
99 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Heat detector is installd in pantry & kitchen | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
100 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is FAPA system genrarated report is available and recived | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
101 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Smoke Detector with RI is installed below False flooring in main Critical/server /HUb rooms | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
102 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Main Fire panel installed and working condition without fault condition | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
103 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is all FAPA is system is connected Main Fire panel and working condition with Proper addressing | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
104 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is PA system Floorwise, Zonal wise to be Provided | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
105 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Sprinkler is installed as per the RCP drawings | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
23 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Fire Safety | Is all sprinkler line valves are open condtion | Open | Open juction box to be closed in Ws. | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
107 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Sprinkler line drain provision need to be check for drain out | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
108 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | In Critical room area sprinkler line should not come | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
109 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | As per NBC sprinklerline height from ceiling if 800 mm above means above upright sprinkler need to be installed | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
110 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Fapa Isolator module provided or not for safety pupose | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
111 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Keys and Lock is available in FHS door | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
112 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is FHS is nozzle & hose is placed with acceeies | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
113 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Gas leakage detection system for gas bank and working condition in Cafeteria,kitchen | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
114 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Glands needs to be provide for Detectors and speakers | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
24 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | Mr cabin | Fire Safety | FAPA panel cupboard glass door frosting needs to be done | Open | MR cabin 2 ( Frosting to be rectified). | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
116 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | FAPA Integration required for Builder panel and Indiqube panel | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
117 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is relly Module with grouping is provided or not for Future any integration, AHU room, Server room, Near Flow switches | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
118 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Integration requried for Access control system, Ac units and other system with working condition | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
119 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Fire proof door is installed in all critical rooms All Critical rooms | Open |  | Medium |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
120 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Is Sprinkler bulb installed 79 in Kitchen and More Heat producing space | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
121 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Is provision is made for access control cable work in main entrance door | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
122 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Is EDR (emmergency Door reliver is available If access is installed | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
123 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Is magnetic system is working properly if access is provided and proper cable dressing | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
124 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Is access control reader is working | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
125 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Is Access control systtem integrated to Fire panel or not | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
25 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | Mr cabin | Furniture | Is all Door is installed as per drawing and working condition with locks | Open | 1 no of door not closing (MR cabin 3). | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
127 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is there is no noise from the door, alligned properly with all inges screws | Open |  | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
128 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is door gasket is installed to all glass meeting rooms | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
26 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Furniture | Is Push and Pull sticker installed in all Door | Open | Sticker to be installed. | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
130 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is all the door handles are fixed properly with proper tightness | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
131 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is Door stopper is installed in required places | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
27 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Furniture | Is Automatic door bottom curtain is installed | Open | 6 pax - Missed table bottom bush to be installed. | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
133 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is glass froasting is done or not as per the design | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
134 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is Main door Client logos are installed | Open |  | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
28 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Furniture | Is Door Glass and aluminium frame scratches free condition | Open | Scratches to be rectified at workstation. | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
136 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is All door keys is working condition and Handed over to FM/Client | Open |  | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
137 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is workstation and pedastal installed as per the Drawings/Design without damages | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
29 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Furniture | Is the workstation glass partition is fixed firmly without any damages | Open | Table wobbling - Workstation. | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
139 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is raceways lines are finished properly without any carpet hanging out | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
140 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is Pedestal locks and keys are working properly and Handed over FM | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
141 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is the cable manager is covered properly with proper Cable raceway | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
142 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is chairs have been placed as per the standard | Open |  | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
30 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | Mr cabin | Furniture | Is Chair adjustment,wheels, Handrest are functioning properly without any damages | Open | MR cabin -1 ( Writing board slightly damagedd). | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
31 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Furniture | Is Modestay panel is installed in - all Workstation | Open | Modesty to be installed in workstation. | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
145 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is all work station and meeting room vertical cable tray installed or not | Open |  | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
146 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is the Locks for Pantry storage and cupboard is provided | Open |  | Medium |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
147 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is Sharp edges needs to be nosing ( DB'S, Cainb cupboards, Pantry Cupboards and Table Corners ) | Open |  | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
148 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Water dispensers should not keep on the floor carpet(work station area) | Open |  | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
149 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Check the availability of the Data and Voice Port points as per the Drawings/Design | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
150 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Check the availability of LAN connection for all workstations. | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
151 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Check the availability of the Network port for the RFS system near rest room | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
152 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Lan connection availability for meeting rooms. | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
153 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Check the availability of loose wires | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
154 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Cable routing is done properly | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
32 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Network | backbone cable is done from indiqube hub room | Open | Gum strain mark to be removedd - Facility 7/25/26, 11:30 AM - Nasar Indiqube added Suresh Projects IQ. | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
156 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Check the availability of LAN connection for printer | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
157 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Wifi lan cable available | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
158 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Wifi Router is installed and internet connectivity working | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
159 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | All the network face plate with numbering need to be install properly with eary accessible condition as per drawing/standard | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
160 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | CCTV in common area and client space if required | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
161 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Check the availability of Dummy's in Faceplate which is not using in the Faceplate | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
162 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Check if there is a provision given to connect the projectors from ceiling to floor | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
163 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | HDMI cable needs to be lay from powerpoint to meeting table | Open |  | Medium |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
33 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Interior | Is all floor is even condition | Open | 2 pax - Uneven floor to be rectified. | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
165 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is carpet is firmly fixed without dust (before installed dust ) | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
166 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is raceways connectors are covered properly | Open |  | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
34 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Interior | Is the corner skirting if fixed properly without gap with rubber | Open | 4 pax room - Gap to be closed properly. | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
35 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Interior | Is carpet have been fixed properly at all corners without gaps | Open | 4 pax - Carpet issue to be rectified. | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
36 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | Mr cabin | Interior | Is floor tiles are fixed properly without Damaged and same colour Including False flooring tiles | Open | Damagedd tiles to be replacedd - MR cabin 1. | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
170 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is transition profile has been fixed in required places | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
37 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Interior | Is Lvt tiles layed properly without any undulation | Open | 4 pax - Tiles alignment required. | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
172 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is Grouting is completed for all floor Tiles done or not and hallow sound coming or nor to be check | Open |  | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
173 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is there is any seepage and water leakages found in the ceiling | Open |  | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
38 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Interior | Is the All wall painting is done properly | Open | DB area - Painting touching up required. | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
175 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is wall papers have been fixed neatly | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
39 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Cleaning | Is no paint stains in the wall paper | Open | Workstation - Paint touch up required. | Medium |  |  |  |  | Ever green | Project SPOC | Transition SPOC
40 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | Mr cabin | Interior | Is ensuring that there is no crack in the wall | Open | MR cabin 3 - Crack portion to be rectified. | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
41 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Rodent entry point | Is all Holes has been closed in Wall and Is all rodent entry point is closed | Open | Gap to be closed. | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
179 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is all False ceiling tiles are fixed properly without stains with proper support | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
180 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is all pipes and fixtures have been painted as per the ceiling colour | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
181 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is grid ceiling support is provided | Open |  | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
182 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is facade Glass is good condition with clean without any damages | Open |  | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
183 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is found there is any leakage from the façade | Open |  | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
184 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is all Openable Facade windows have been locked with proper Lock | Open |  | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
185 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is Façade bottom partition to be close floor to floor (Fire sealent ) | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
42 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Interior | Is Façade glass installed all area and same type of glass installed with cleaning without gaps | Closed | Acoustic has been closed for temporary ( Glass will be installed by tomorrow as per PM update) @⁨vineeth bisaa⁩ fyi. | Medium |  |  | 25/07/2026 |  | Interior | Project SPOC | Transition SPOC
187 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is Gaps should not available in door to frames | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
188 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is the Blinds for window and required place with proper roller is installed | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
189 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is all blinds are functioning properly | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
190 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is Glass writing board if fixed properly properly without any Damaged in all enclosed cabin | Open |  | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
43 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | Mr cabin | Interior | Is Accoustic is installed all in cabin as per the design without any gaps | Open | MR cabin 2 ( Side gap to be rectified). | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
44 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Interior | Is Sound proff cabin to cabin to be checked | Open | Meeting cabin Fascad window to be rectified. | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
45 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Interior | Is Client Cafeteria or Terrace Balcony area drain line needs to check | Open | Leak observed in drain line - FHS during charging. | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
194 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Parking | Is Parking marking with Numbering is done | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
195 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is bundwall is avabile in cafeteria area rain water doesn't enter to inside building | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
46 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Interior | Is Drain provision provided in the pantry area for coffee machine with drainline | Open | Gum strain mark to be removedd - Facility. | High |  |  |  |  | Interior | Project SPOC | Transition SPOC
197 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is pillar gaurd installed in all columns | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
198 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Furniture | Is List available for Indiqube scope and Client scope details | Open |  | High |  |  |  |  | Imported & Featherlite | Project SPOC | Transition SPOC
199 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Signages | Is Client name add in the VMS | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
47 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Signages | Is Rest room signages to be installed | Open | Door push -pull signage to be installed. | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
201 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Signages | Is Client Name is installed in client Directory board | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
202 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Parking | Is parking signages with allocation | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
48 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Cleaning | Is all are Deep cleaning is completed | Open | Filter cleaning required. | Medium |  |  |  |  | Ever green | Project SPOC | Transition SPOC
49 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Cleaning | Is All above ceiling Height cleaning is done | Open | Above ceiling cleaning required. | Medium |  |  |  |  | Ever green | Project SPOC | Transition SPOC
205 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Cleaning | Is All Project unused and unwanted material is cleares in client space and client Parking area | Open |  | High |  |  |  |  | Ever green | Project SPOC | Transition SPOC
206 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Landscaping | is Landscaping work is completed | Open |  | High |  |  |  |  | Builder | Project SPOC | Transition SPOC
207 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Landscaping | Is Landscaping work - Amc is available status (Yes/No) (1 month - Free Warranty for client space) | Open |  | High |  |  |  |  | Builder | Project SPOC | Transition SPOC
208 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Landscaping | Is all meteeing room Ceramic planter pot placed | Open |  | Medium |  |  |  |  | Builder | Project SPOC | Transition SPOC
209 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is Glass door and Partition glasses free from scratches | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
210 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | Is all Chinna table and indiqube branding is done from Asset team | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
211 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network | Ensure all client space/common area access control access - access card needs to be provided Facility/Security if dedicated security is not available | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
212 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Service | Is all service to be ensure as per the serivce subrication | Open |  | High |  |  |  |  | Service team | Project SPOC | Transition SPOC
213 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Service | Is water service is available | Open |  | Medium |  |  |  |  | Service team | Project SPOC | Transition SPOC
214 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Service | Is Pestcontrol is service done or not | Open |  | High |  |  |  |  | Service team | Project SPOC | Transition SPOC
215 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | UPS load to be checked in UPS - After client onboarding load to be ensure mention here | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
216 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Thermography Testing to be done By the electrical vendors after the client Onboarding checklist | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
217 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Interior | As per Final approval Layout all asset ,losse furniture and designer Elements to be install | Open |  | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
50 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Interior | Check the all cabins duster holder needs to be install without Damages | Open | 4 pax - Duster holder to be installed. | Medium |  |  |  |  | Interior | Project SPOC | Transition SPOC
219 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical HOD | Electrical As built drawings, Warranty certificates, Lux level report , commissioing report to be submits | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
220 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac HOD | Hvac As built drawings, Warranty certificates, Co2, CFM level report , commissioing report to be submits | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
221 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety HOD | Hvac As built drawings, Warranty certificates, system genarated report , commissioing report to be submits | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
222 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Network HOD | Network As built drawings, Warranty certificates, fluke test report , commissioing report to be submits | Open |  | High |  |  |  |  | Nikhita | Project SPOC | Transition SPOC
223 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Ensure Electrical demo activity is completed and mail has been shared to FM | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
224 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Hvac | Ensure Hvac demo activity is completed and mail has been shared to FM | Open |  | High |  |  |  |  | IND Aircon | Project SPOC | Transition SPOC
225 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Fire Safety | Ensure FAPA demo activity is completed and mail has been shared to FM | Open |  | High |  |  |  |  | V3 automation | Project SPOC | Transition SPOC
51 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Cleaning | Ensure cleaning is completed inside the Fire shaft,Plumbing shaft and Electrical shaft | Open | Cleaning required panel top side. | High |  |  |  |  | Ever green | Project SPOC | Transition SPOC
227 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F |  | 5F | All area | Electrical | Ensure Meggar testing is done for cables | Open |  | High |  |  |  |  | MD Electrical | Project SPOC | Transition SPOC
228 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
229 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
230 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
231 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
232 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
233 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
234 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
235 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 25/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
236 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
237 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
238 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
239 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
240 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
241 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
242 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
243 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium | Media file not included in ZIP export |  |  |  | TBD | Project SPOC | Transition SPOC
244 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
245 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium | Media file not included in ZIP export |  |  |  | TBD | Project SPOC | Transition SPOC
246 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
247 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium | Media file not included in ZIP export |  |  |  | TBD | Project SPOC | Transition SPOC
248 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
249 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium | Media file not included in ZIP export |  |  |  | TBD | Project SPOC | Transition SPOC
250 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
251 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
252 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC
253 | Subramanya arcade T 1 -Nxgen -5F | Subramanya arcade T 1 -Nxgen -5F | 26/07/2026 | 5F | All area | Unassigned |  | Open |  | Medium |  |  |  |  | TBD | Project SPOC | Transition SPOC

## Summary
Snaglist Summary Dashboard
Key Metrics |  |  | Status Overview
Metric | Value |  | Status | Count
Total Snags | 253 |  | Open
Matched | 51 |  | Closed
Unmatched | 202
Unmatched Snags | 26
Match Rate
Open | 251
Closed | 2
Category Distribution |  |  |  |  | Priority Breakdown
Category | Count | % |  |  | Priority | Count
Hvac | 53 |  |  |  | Medium | 155
Electrical | 36 |  |  |  | High | 98
Interior | 36
Fire Safety | 34
Unassigned | 26
Furniture | 25
Network | 21
Cleaning | 5
Signages | 3
Landscaping | 3
Service | 3
Rodent entry point | 2
Parking | 2
Electrical HOD | 1
Hvac HOD | 1
Fire Safety HOD | 1
Network HOD | 1
TOTAL
Vendor Distribution
Vendor | Count
IND Aircon | 54
V3 automation | 38
MD Electrical | 37
Interior | 36
Nikhita | 26
TBD | 26
Imported & Featherlite | 25
Ever green | 5
Builder | 3
Service team | 3

## Correction Notes
Field | Original | Corrected
Check Points | Emeregency | Emergency
Check Points | allignment | alignment
Check Points | achiving | achieving
Check Points | Draiwings | Drawings
Check Points | Lighining | Lighting
Check Points | temparary | temporary
Snag Points | installedded | installed
Check Points | obstuction | obstruction
Check Points | scoket | socket
Snag Points | fixeded | fixed
Check Points | awarness | awareness
Check Points | signgages | signages
Check Points | engish | English
Check Points | stips | strips
Check Points | Exhuast | Exhaust
Check Points | Diffueser | Diffuser
Check Points | Landscapping | Landscaping